## Slide 1: Displacement Ventilation

## Slide 2: Displacement Ventilation
Overview and Benefits
Common Applications
Design Considerations
Selection Process and Tools
Custom Considerations
Agenda

## Slide 3: Overview and Benefits

## Slide 4: Displacement Ventilation
Review of Mixing Systems
55ºF supply air
Mix the entire space
Diffusers drive air motion
High velocity supply
Overview and Benefits

## Slide 5: Displacement Ventilation
Displacement Systems
65-68ºF supply air
Low velocity
No mixing in space
Heat sources drive air motion
Stratified heat, contaminants
Only conditions the occupied zone
Overview and Benefits

## Slide 6: Displacement Ventilation
How DV Works:
Thermal Plumes:
  Create temperature stratification
  Carry contaminants from breathing zone
  Improve air quality in occupied zone
Overview and Benefits

## Slide 7: Displacement Ventilation
Thermal Plumes
Heat sources drive air motion
Overview and Benefits
Notes: Diffusers no longer momentum source

## Slide 8: Displacement Ventilation
Stratification – How much is comfortable?
ASHRAE 55- 7.2°F (standing) allowed
  Addendum A (2013)
More is possible
Overview and Benefits
Source: CBE

## Slide 9: Displacement Ventilation
Flexibility
Quiet
Indoor Air Quality
Thermal Comfort
Occupant Performance
Energy Savings
LEED and CHPS
Overview and Benefits

## Slide 10: Displacement Ventilation
IEQ- Indoor Environmental Quality
Air Quality
  Stratification
Thermal Comfort
  Higher SAT, Lower Velocities
Acoustics
  Lower velocities
  Low static pressures
Overview and Benefits
Notes: Improve productivity through improvements in IEQ

## Slide 11: Displacement Ventilation
Zone Air Distribution Effectiveness (Ez)
A measure of how effectively the zone air distribution uses its supply air to maintain acceptable air quality in the breathing zone. ASHRAE 62.1.
Overview and Benefits
Notes: The air change effectiveness (ACE), is defined as the age of air that would occur throughout the room if the air was perfectly mixed, divided by the average age of air where occupants breathe. The age of air at a particular location is the average time elapsed since molecules of air at that location entered the building. Because the average age of air exiting the room is identical to the age of air that would occur throughout the room if the indoor air were perfectly mixed, the ACE is also the exhaust-air age divided by the average age of air where occupants breathe. In practical terms, the ACE equals the effective ventilation rate at the breathing zone divided by the ventilation rate that would occur throughout the building with perfect mixing and at the same outdoor air supply. A short-circuiting flow pattern between the air supply diffusers and return grilles, increases the room-air age and causes ACE to be less than unity. Perfect mixing results in an ACE of unity. Preferentially ventilating the breathing zone with outside air will cause the ACE to be greater than unity.

## Slide 12: Displacement Ventilation
Overview and Benefits
Ez = 1.0
Ez = 1.2

## Slide 13: Displacement Ventilation
Overview and Benefits

## Slide 14: Displacement Ventilation
Air-Change Effectiveness (ACE)
A comparison of the age of air in the occupied portions of the building to the age of air that would exist under conditions of perfect mixing of the ventilation air. ASHRAE 129-1997
Overview and Benefits
From ASHRAE 62.1 2013
Notes: The air change effectiveness (ACE), is defined as the age of air that would occur throughout the room if the air was perfectly mixed, divided by the average age of air where occupants breathe. The age of air at a particular location is the average time elapsed since molecules of air at that location entered the building. Because the average age of air exiting the room is identical to the age of air that would occur throughout the room if the indoor air were perfectly mixed, the ACE is also the exhaust-air age divided by the average age of air where occupants breathe. In practical terms, the ACE equals the effective ventilation rate at the breathing zone divided by the ventilation rate that would occur throughout the building with perfect mixing and at the same outdoor air supply. A short-circuiting flow pattern between the air supply diffusers and return grilles, increases the room-air age and causes ACE to be less than unity. Perfect mixing results in an ACE of unity. Preferentially ventilating the breathing zone with outside air will cause the ACE to be greater than unity.

## Slide 15: Displacement Ventilation
Indoor Air Quality (IAQ)
1.0 = perfectly mixed
Higher ACE with DV
Stratified contaminants
Fresh air delivered at low level
Overview and Benefits
At heat source
Source: Jung and Zeller, 2005.
Improvement over mixed
Notes: The air change effectiveness (ACE), is defined as the age of air that would occur throughout the room if the air was perfectly mixed, divided by the average age of air where occupants breathe. The age of air at a particular location is the average time elapsed since molecules of air at that location entered the building. Because the average age of air exiting the room is identical to the age of air that would occur throughout the room if the indoor air were perfectly mixed, the ACE is also the exhaust-air age divided by the average age of air where occupants breathe. In practical terms, the ACE equals the effective ventilation rate at the breathing zone divided by the ventilation rate that would occur throughout the building with perfect mixing and at the same outdoor air supply. A short-circuiting flow pattern between the air supply diffusers and return grilles, increases the room-air age and causes ACE to be less than unity. Perfect mixing results in an ACE of unity. Preferentially ventilating the breathing zone with outside air will cause the ACE to be greater than unity.

## Slide 16: Displacement Ventilation
Benefits of increased IAQ
Occupant health
Decreased absenteeism
Staff retention
Student/employee performance
Overview and Benefits

## Slide 17: Displacement Ventilation
CHPS
Focuses on occupant health and reducing operating costs
Preferred air distribution method
Awards up to 4 points for the use of DV
Overview and Benefits

## Slide 18: Displacement Ventilation
Overview and Benefits

## Slide 19: Displacement Ventilation
Two-year study of symptoms in students
69% reduction in asthmatic symptoms in schools with new DV
Study performed in 39 schools -12 schools implemented new DV systems
Overview and Benefits
Source: Smedje and Norback, 2000
Number of Incidents

## Slide 20: Displacement Ventilation
Majority of focus on building design is energy savings, however:
  Energy accounts for less than 10% of average owner operating cost
  1% productivity increase equivalent to 18% energy savings
Focus on creating comfortable environments
Overview and Benefits
Chart: Operating Costs
| Employee | Energy | O&M | Rent
Sales | 89 | 5 | 3 | 4
Sales | 89 | 5 | 3 | 4 | 0

## Slide 21: Displacement Ventilation
Productivity
CBE’s Occupant Survey Database
  Over 16,000 people
  119 buildings
DV systems can help improve largest influencing factors for occupant productivity
Overview and Benefits
Source: CBE, Productivity and IEQ Satisfaction

## Slide 22: Displacement Ventilation
Productivity
CBE’s Occupant Survey Database
  Over 16,000 people
  119 buildings
DV systems can help improve largest influencing factors for occupant productivity
Overview and Benefits
Source: CBE, Productivity and IEQ Satisfaction
Top 3

## Slide 23: Applications

## Slide 24
Education
Happy valley middle school

## Slide 25
AUDITORIUMS
Kauffman center

## Slide 26
INDUSTRIAL
SOLAR WINDS PLANT

## Slide 27
HEALTHCARE
KAISER MODESTO

## Slide 28
airports
San Francisco t2

## Slide 29
CASINOS
EDGEWATER CASINO

## Slide 30: Design Considerations

## Slide 31: Displacement Ventilation
Air Volume Calculations
Design Guide
  ASHRAE research
Based on zones with approx. 9 ft. ceiling height
Calculate:
  Supply Air Volume
  Supply Air Temperature
  Exhaust Air Temperature
Design Considerations

## Slide 32: Displacement Ventilation
Air Volume Calculations
Standard heat transfer equation not applicable
Assumes complete mixing
DV only conditions the occupied zone
Design Considerations

## Slide 33: Displacement Ventilation
Three components of load
qoe – Occupants / Equipment
qL – Overhead Lighting
qex – Solar / Envelope Loads
Design Considerations

## Slide 34: Displacement Ventilation
Air Volume Calculations
For sensible loads only
Room load coefficients:
  Occupants/Equipment (aoe) = 0.295* qoe
  Overhead Lighting (al) = 0.132* qL
  Conduction/Radiation (aex) = 0.185* qex
Design Considerations
Source: ASHRAE RP-949 (Chen et al. 1999)

## Slide 35: Displacement Ventilation
Example space loads and qualifications
Area: 750 ft2
Room Temperature Set Point: 74ºF
Room Dimensions: 25 ft. x 30 ft. x 10 ft.
Window Area: 100 ft2
Design Considerations

## Slide 36: Displacement Ventilation
Example space loads and qualifications
1 instructor
25 students
  qo: 26 x 250 Btu/h = 6500 Btu/h
3 computers w/ LCD monitors
  qe: 3 x 308 Btu/h = 924 Btu/h
T8 florescent lighting
  ql = 750 ft2 x 6.826 Btu/h/ft2 = 5120 Btu/h
qex = 300ft2 x 14.6 Btu/h/ft2 = 4381 Btu/h
qtotal = 16,925 Btu/h
Design Considerations

## Slide 37: Displacement Ventilation
Ventilation required by ASHRAE 62.1-2007
0.12 cfm/ft2 (outdoor air)
10 cfm/person (outdoor air)
Fully Mixed
Ventilation effectiveness: Ez = .80
𝑄𝑜𝑧=(𝑅𝑝 𝑃z+𝑅𝐴 𝐴𝑧)/𝐸𝑧 =(10*26+0.12*750)/.80 = 438𝑐𝑓𝑚
Stratified (DV)
Ventilation effectiveness: Ez = 1.2
𝑄𝑜𝑧=(𝑅𝑝 𝑃𝑧+𝑅𝐴 𝐴𝑧)/𝐸𝑧 =(10*26+0.12*750)/1.2 = 292 𝑐𝑓𝑚
Design Considerations

## Slide 38: Displacement Ventilation
Airflow required by ASHRAE 62.1-2007
Qmix load =qOE+ qL +qEX /60𝜌cp∆t
=16925/(1.08)(74–55)=824 cfm
Design Considerations

## Slide 39: Displacement Ventilation
Airflow calculations for DV
  QDV=(0.295*7424+0.132*5120+0.185*4381)/60(0.075)(0.24)7.2
  QDV= 473cfm
473 cfm vs. 824 cfm for cooling
43% reduction in air volume
33% reduction in outdoor air
Design Considerations
 | Displacement Systems | Overhead / VRF System
Outdoor Air | 292cfm | 438cfm
Cooling Air | 473cfm | 824cfm

## Slide 40: Displacement Ventilation
Performance Data:
Influences selection and layout
Standards:
Adjacent zone (Nordtest)
Draft Rate (DR)- ASHRAE 55-2004 & ISO 7730
Standard Effect Temperature (SET)- ASHRAE 55-2010
Design Considerations

## Slide 41: Displacement Ventilation
Adjacent Zone
What does it mean?
  Measured at 1” (Nordtest) or 4” above the floor in which the air velocity is at least 40 fpm
  Defines velocity profile of diffuser
What is an acceptable adjacent zone length?
  Shorter or longer?
  Shorter means lower air quality
  Longer means lower comfort
  No defined acceptable range
Design Considerations

## Slide 42: Displacement Ventilation
Draft Rate (DR)
Comfort based metric
  ASHRAE 55-2004
  ISO 7730-2005
Predicts the percentage of people dissatisfied due to draft based on:
  Air Velocity
  Air Temperature
  Turbulence Intensity
Defined limits:
  DR<20% acceptable
Design Considerations
>20% DR
<20% DR Comfort Zone

## Slide 43: Displacement Ventilation
Face velocities
Face velocity (~40 fpm)
No throw, drop, collision, etc. to consider
Low noise
Low pressure drop
Design Considerations

## Slide 44: Displacement Ventilation
Duct sizing
Similar to conventional system
Limit inlet to 1000 fpm
Increased face area, reduced face velocity
Design Considerations

## Slide 45: Displacement Ventilation
Heating with Displacement
Design Considerations
2-10ºF Cooling
0-5ºF Heating
5ºF+ Heating

## Slide 46: Diffuser Selection Process

## Slide 47: Displacement Ventilation
Steps to Selecting Displacement Diffuser
  Determine total square footage of diffuser required
    Face velocity for 40fpm
    Inlet sized for ~800fpm inlet velocity
  Determine type(s) of diffuser
    Where will diffuser be installed?
  Determine if any customization is required
    Color
    Size
    Install method
Diffuser Selection Process

## Slide 48: Displacement Ventilation
  Determine size of diffuser
    Face velocity for 40fpm
    Inlet sized for ~800fpm inlet velocity
  Determine type(s) of diffuser
    Where will diffuser be installed?
  Determine if any customization is required
    Color
    Size
    Install method
Diffuser Selection Process

## Slide 49: Displacement Ventilation
Conference Room requires 216CFM
  Square footage of diffuser required:
  Minimum inlet size of diffuser:
  Type of Diffuser:
Diffuser Selection Process– Example
Mixing
Airflow: 277 CFM
Diffuser:
  24” x 24“ SPD
5.4 sqft
2.5” x 15”
Notes: 150cfm -200cfm per Sq diffuser
23 x 36 DFW

## Slide 50: Displacement Ventilation
Overhead Displacement
Familiar/easy install
Standard heat/cool switchover option
Ideal in spaces with limited wall space
Ideal in wide open spaces
Location of diffusers critical to minimize draft
Overhead Displacement vs Sidewall Displacement
Sidewall Displacement
More complex install and more duct work required
Standard cooling only
Limited by the wall space available
Higher flexibility with location of diffusers

## Slide 51: Diffuser Selection Process Custom Considerations

## Slide 52: Displacement Ventilation
Wide variety of Price standard displacement diffusers
  Wall / ceiling mounted
  Floor mounted
  Heat / cool models
  Industrial models
Custom Considerations

## Slide 53: Displacement Ventilation
Custom Diffuser Options
  Color
  Size
  Material
  Architectural integration
  Perforation pattern
  Fastening system
Custom Considerations

## Slide 54: Displacement Ventilation
Information to provide for most Common Specials
  Color
    Provide RAL color or color chip sample (preferred)
  Oversized units
    Inlet dimensions to minimize noise (< 1000fpm)
  DFR with Plenum
    Specify plenum depth and inlet size
  Curved diffusers
    Specify the length of arc
    Specify the radius of curvature
Custom Considerations

## Slide 55: Displacement Ventilation
Custom Considerations

## Slide 56: Displacement Ventilation
Steps to Selecting Displacement Diffuser
Selection Process
  Determine the size of diffuser required
    Typically sized for 40fpm
    Inlet sized for ~800fpm inlet velocity
  Determine type(s) of diffuser
    Where will diffuser be installed?
  Determine if any customization is required
    Color
    Size
    Install method

## Slide 57: Displacement Ventilation
Custom Considerations

## Slide 58: Displacement Ventilation
High Performance School Microsite
https://pricevm.com/schools

## Slide 59: Displacement Ventilation
Curved Diffusers
Products

## Slide 60: Displacement Ventilation
Installation examples
Products
DR360-DH
DR360-DH

## Slide 61: Displacement Ventilation
Installation examples
Products
DLE-H
Lunchroom / cafeteria
DLE-H
Office

## Slide 62: Displacement Ventilation
Custom diffuser highlights
Products
Custom column wrapped DR180
DR360 with custom hinged face and electrical integration
Notes: The custom DR180’s in this school cafeteria are also used as a base for a condiment/napkin stand. As you can see, the kids are seated very close to the diffusers – a great example of the high thermal comf

## Slide 63: Displacement Ventilation
DFGL
Products
DFGL

## Slide 64: Displacement Ventilation
Custom curved DFW with heat/cool
Products
DFW with custom size, perforation, color, and fasteners

## Slide 65
Concourse features custom diffusers integrated into the wall and 360° flow diffusers

## Slide 66: Displacement Ventilation
Displacement Ventilation in International Terminal
Vancouver International Airport

## Slide 67
Gerald Ford International AP
Grand Rapids, MI

## Slide 68
San Francisco airport T2
Architect: Gensler
Engineer: SJ Engineers

## Slide 69
Custom geometries and finishes were used to integrate diffusers into the aesthetics of the terminal. Here, the diffuser is located in the right hand corner of the back wall

## Slide 70
Displacement diffusers are hidden within the bases of arrival/departure boards, display cases, and counters
Notes: Stainless steel diffusers with a custom face. Curved. Price worked closely with design team on this job – went very smoothly.

## Slide 71
Displacement diffusers are hidden within the bases of arrival/departure boards, display cases, and counters

## Slide 72: Displacement Ventilation Questions?

## Slide 73: Displacement Ventilation
https://www.priceindustries.com/software/room-designer/
Design Support

## Slide 74: Displacement Ventilation
Price Room Designer Software
Complete load calculations in Trace
  Use basic mixing module
Input peak sensible loads into software
  Latent load conditioned at AHU
Determine air volume for DV
Design Support

## Slide 75: Displacement Ventilation
Computational Fluid Dynamics
Simulates system performance
Variety of data outputs
  Temperature
  Velocity
  Thermal comfort
  IAQ
System optimization
Design Support

## Slide 76: Displacement Ventilation
Verify system performance
Simulate working conditions
  Hot/cold wall
  Adjustable ceiling height
  Raised floor
Can be used in conjunction with CFD modeling
Design Support
Church Retrofit Mock-up
Classroom Mock-up

## Slide 77: Questions?